## Ark1
Case 1 |  | Tilstand 1 |  | Tilstand 2 |  | Tilstand 3 |  | Tilstand 4
|  | Start tilstand | 20s efter udkobling | Start tilstand | 20s efter udkobling | Start tilstand | 20s efter udkobling | Start tilstand | 20s efter udkobling
Powerplant | P(MW) | 5.5 | 5 | 4.621 | 4.312 | 3.798 | 3.616 | 2.995 | 2.946
| Q(MVar) | 1.1 | 1.5 | 0.308 | 0.571 | -0.32 | -0.126 | -0.931 | -0.786
| V(pu) | 1 | 1.01 | 1 | 0.99 | 1 | 0.98 | 1 | 0.98
Transmission central 60kV busbar | V(pu) | 1 | 1.01 | 1 | 0.99 | 1 | 0.98 | 1.01 | 0.98
Town1 busbar | V(pu) | 1 | 0.99 | 1.01 | 0.99 | 0.99 | 0.97 | 1 | 0.98
Town2 busbar | V(pu) | 0.99 | 0.97 | 1.01 | 0.98 | 0.99 | 0.97 | 1 | 0.98
Town3 busbar | V(pu) | 0.99 | 0.96 | 1.01 | 0.98 | 1 | 0.97 | 1 | 0.98
Town4 busbar | V(pu) | 0.99 | 0.93 | 1 | 0.96 | 0.99 | 0.97 | 1.01 | 1
Town5 busbar | V(pu) | 1 | 0.9 | 1 | 0.94 | 1 | 0.97 | 1 | 1.01
Battery town4 | P(MW) | disc. | disc. | 0.25 | 0.25 | 0.5 | 0.487 | 0.75 | 0.747
| Q(MVar) | disc. | disc. | 0.121 | 0.121 | 0.242 | 0.236 | 0.363 | 0.362
Battery town5 | P(MW) | disc. | disc. | 0.5 | 0.5 | 1 | 0.973 | 1.5 | 1.514
| Q(MVar) | disc. | disc. | 0.242 | 0.242 | 0.484 | 0.471 | 0.726 | 0.733
Big disturbance w. decentral batterieries, 60kV transmissions cable out for maintanence, loss of Windfarm (2MW and pf 0,95), full load (1,5MW and pf 0,95) |  | 1 |  | 2 |  | 3 |  | 4 |  | Big disturbance w. central batterypark, 60kV transmissions cable out for maintanence, loss of Windfarm (2MW and pf 0,95), full load (1,5MW and pf 0,95) |  | 1 |  | 2 |  | 3 |  | 4
|  | initial condition | 20sec after fault | initial condition | 20sec after fault | initial condition | 20sec after fault | initial condition | 20sec after fault |  |  | initial condition | 20sec after fault | initial condition | 20sec after fault | initial condition | 20sec after fault | initial condition | 20sec after fault
Powerplant | P(MW) | 5.621 | 5.289 | 2.749 | 2.911 | 0.121 | 0.976 | -1.596 | 0.137 | Powerplant | P(MW) | 5.621 | 5.289 | 3.102 | 3.269 | 0.603 | 1.367 | -1.135 | 0.227
| Q(MVar) | 0.827 | 1.005 | -1.532 | -0.951 | -3.28 | -2.398 | -4.164 | -3.536 |  | Q(MVar) | 0.827 | 1.005 | -0.676 | -0.286 | -1.977 | -1.414 | -2.724 | -2.13
| V(pu) | 1 | 0.85 | 1 | 0.84 | 1 | 0.86 | 1 | 0.98 |  | V(pu) | 1 | 0.85 | 1 | 0.85 | 1 | 0.88 | 1 | 0.94
Transmission 60kV busbar | V(pu) | 1 | 0.85 | 0.99 | 0.83 | 1 | 0.87 | 1.01 | 0.98 | Transmission 60kV busbar | V(pu) | 1 | 0.85 | 1 | 0.86 | 1 | 0.88 | 1 | 0.93
Town 1 | V(pu) | 1 | 0.85 | 0.99 | 0.84 | 1 | 0.88 | 1.01 | 0.99 | Town 1 | V(pu) | 1 | 0.85 | 1 | 0.86 | 1.01 | 0.89 | 0.99 | 0.93
Town 2 | V(pu) | 1.01 | 0.85 | 0.99 | 0.84 | 1 | 0.88 | 1 | 0.98 | Town 2 | V(pu) | 1.01 | 0.85 | 1.01 | 0.86 | 1 | 0.89 | 1 | 0.94
Town 3 | V(pu) | 1.01 | 0.85 | 0.99 | 0.84 | 1 | 0.88 | 1 | 0.98 | Town 3 | V(pu) | 1.01 | 0.85 | 1 | 0.86 | 1 | 0.88 | 1 | 0.93
Town 4 | V(pu) | 1.01 | 0.85 | 0.99 | 0.84 | 1 | 0.88 | 1 | 0.98 | Town 4 | V(pu) | 1.01 | 0.85 | 1.01 | 0.86 | 1 | 0.89 | 1 | 0.94
Town 5 | V(pu) | 1 | 0.85 | 0.99 | 0.84 | 1 | 0.88 | 1.01 | 0.99 | Town 5 | V(pu) | 1 | 0.85 | 1 | 0.86 | 1.01 | 0.89 | 0.99 | 0.93
Battery 1 | P(MW) | disc | disc | 0.5 | 0.425 | 1 | 0.884 | 1.35 | 1.323 | Battery 1 | P(MW) | disc | disc | disc | disc | disc | disc | disc | disc
| Q(MVar) | disc | disc | 0.242 | 0.206 | 0.484 | 0.428 | 0.654 | 0.641 |  | Q(MVar) | disc | disc | disc | disc | disc | disc | disc | disc
Battery 2 | P(MW) | disc | disc | 0.5 | 0.425 | 1 | 0.884 | 1.35 | 1.323 | Battery 2 | P(MW) | disc | disc | disc | disc | disc | disc | disc | disc
| Q(MVar) | disc | disc | 0.242 | 0.206 | 0.484 | 0.428 | 0.654 | 0.641 |  | Q(MVar) | disc | disc | disc | disc | disc | disc | disc | disc
Battery 3 | P(MW) | disc | disc | 0.5 | 0.425 | 1 | 0.884 | 1.35 | 1.323 | Battery 3 | P(MW) | disc | disc | disc | disc | disc | disc | disc | disc
| Q(MVar) | disc | disc | 0.242 | 0.206 | 0.484 | 0.428 | 0.654 | 0.641 |  | Q(MVar) | disc | disc | disc | disc | disc | disc | disc | disc
Battery 4 | P(MW) | disc | disc | 0.5 | 0.425 | 1 | 0.884 | 1.35 | 1.323 | Battery 4 | P(MW) | disc | disc | disc | disc | disc | disc | disc | disc
| Q(MVar) | disc | disc | 0.242 | 0.206 | 0.484 | 0.428 | 0.654 | 0.641 |  | Q(MVar) | disc | disc | disc | disc | disc | disc | disc | disc
Battery 5 | P(MW) | disc | disc | 0.5 | 0.425 | 1 | 0.884 | 1.35 | 1.323 | Battery 5 | P(MW) | disc | disc | disc | disc | disc | disc | disc | disc
| Q(MVar) | disc | disc | 0.242 | 0.206 | 0.484 | 0.428 | 0.654 | 0.641 |  | Q(MVar) | disc | disc | disc | disc | disc | disc | disc | disc
[10 empty] | Batterypark | P(MW) | disc | disc | 2.5 | 2.134 | 5 | 4.41 | 6.75 | 6.318
[11 empty] | Q(MVar) | disc | disc | 1.211 | 1.034 | 2.422 | 2.136 | 3.269 | 3.06
Overvoltages, loss of town(1,5MW and pf 0,95). Windfarm(2MW and pf 0,95). Disconnection of town 2 at trafo |  | 1 |  | 2 |  | 3 |  | 4
|  | initial condition | 20sec after fault | initial condition | 20sec after fault | initial condition | 20sec after fault | initial condition | 20sec after fault
Powerplant | P(MW) | 5.502 | 6.095 | 5.502 | 5.338
| Q(MVar) | 0.856 | 0.088 | 0.856 | 0.992
| V(pu) | 1 | 1.15 | 1 | 1.01
Transmission 60kV busbar | V(pu) | 0.99 | 1.15 | 0.99 | 1
Town 1 | V(pu) | 1 | 1.18 | 1 | 1.01
Town 2 | V(pu) | 0.99 | disc | 0.99 | disc
Town 3 | V(pu) | 0.99 | 1.17 | 0.99 | 1
Town 4 | V(pu) | 0.99 | 1.17 | 0.99 | 0.99
Town 5 | V(pu) | 1 | 1.17 | 1 | 0.99
Battery 1 | P(MW) | disc | disc | disc | -0.352
| Q(MVar) | disc | disc | disc | -0.171
Battery 2 | P(MW) | disc | disc | disc | disc
| Q(MVar) | disc | disc | disc | disc
Battery 3 | P(MW) | disc | disc | disc | -0.309
| Q(MVar) | disc | disc | disc | -0.15
Battery 4 | P(MW) | disc | disc | disc | -0.276
| Q(MVar) | disc | disc | disc | -0.134
Battery 5 | P(MW) | disc | disc | disc | -0.307
| Q(MVar) | disc | disc | disc | -0.149